## Sheet1
Item No | Item Description | Quantity | Unit | Rate | Amount
10 | Interior work and terrace beautification
10.1 | Providing and laying Cast in situ/Ready Mix cement concrete in M-25 of trap/ granite/ quartzite/ gneiss metal for R.C.C. beams and lintels as per detailed designs and drawings or as directed including steel centering, formwork, cover blocks, laying/pumping, compactionand roughening the surface if special finish is to be provided and curing etc. complete. (Excluding reinforcement and structural steel). complete. With fine aggregate (Crushed sand VSI Grade) | 3.5 | m3 |  | 0
10.2 | Providing and fixing in position HCRM / CRS (Corrosion Resistant Steel) bar reinforcement of various diameters for R.C.C. pile caps, footings, foundations, slabs, beams columns, canopies, staircase, newels, chajjas, lintels pardis, copings, fins, arches etc. as per detailed designs, drawings and schedules. including cutting, bending, hooking the bars, binding with wires or tack welding and supporting as required complete. | 0.55 | US ton |  | 0
10.3 | Providing second class Burnt brick masonry with conventional/ I.S. type bricks in cement mortar 1:6 in superstructure including striking joints, raking out joints, watering and scaffolding etc. Complete | 20 | m3 |  | 0
10.4 | Providing and laying damp proof course 75 mm thick in M20 cement concrete layer and bitumen / using cement with waterproofing compound curing, formwork etc. complete. Cost to include that for removing one layer of brickwork in alternate segments of about 1.5 meters length & filling the Damp proof course therein. | 17.5 | m2 |  | 0
10.5 | Providing internal cement plaster 12mm thick in single coat in cement mortar 1:3 without neeru finish to concrete or brick surfaces, in all position including scaffolding and curing etc. complete. | 115 | m2 |  | 0
10.6 | Providing sand faced plaster externally in cement mortar using approved screened sand, in all positions including base coat of 15 mm thick in cement mortar 1:4 using waterproofing compound at 1Kilogramper cement bag curing the same for not less than 2 days and keeping the surface of the base coat rough to receive the sand faced treatment 6 to 8 mm thick in cement mortar 1:4 finishing the surface by taking out grains and curing for fourteen days scaffolding etc.complete. | 115 | m2 |  | 0
10.7 | Providing and fixing chicken mesh of 22 gauge, with about 30 cm. width at the junction of R.C.C members and brick work, of approved quality including fixing mesh in position by necessary drilling in concrete /B.B.masonry and or tying by binding wire etc. complete. | 74.5 | m |  | 0
10.8 | Providing and applying plaster / wall punning with plaster of paris ( with plaster of paris material) in 10 to 13 millimeter thickness to previously plastered surface / or on newly brick surface ( Excluding rough cast plaster ) in all position including preparing and Finishing the surface scaffolding etc.complete. | 115 | m2 |  | 0
10.9 | Providing sills in stepped fashion, of required material 20mm to 25mm thick, on a bed of cement mortar 1:4 including cement float, filling joints with neat cement slurry, curing, moulding edges, polishing,cleaning complete. b) Granite, basic Price Rs 125/- per Sqft | 65 | m2 |  | 0
10.1 | Providing and applying pearl/ luster finish paint of approved colour and shade to the existing plaster surface including scaffolding, preparing the surface, applying the acrylic wall putti etc. complete. | 1030 | m2 |  | 0
10.11 | Providing and applying two coats of exterior weather shield paint of approved manufacture and of approved colour to the plastered surfaces including cleaning ,preparing the plaster surface ,applying primer coat ,scaffolding if necessary, and watering the surface for two days etc complete. | 455 | m2 |  | 0
10.12 | Providing and fixing 3.5 to 4 mm thick Veneer finish wall Panaling made out of 50 x 25 mm (finished size) C.C.T.W. frame work or size of 600 x 600 mm center or as per site condition covered by 6 mm thick marine plywood of the generally confiriming to I:S 710-1980 finished with 3.5 to 4 mm thick matching Veneer of approved color and in satin wallnut groov matched veneer pattern and design including melamine polishing and design with antitermite treatment etc. to plywood and woodwork with ten years guarantee bond etc. including all lead and lifts complete. Cost to also include that for exposed vertical battens in TW of size 1.5" x 1" at 600 mm c/c. | 82.5 | m2 |  | 0
10.13 | Providing & Fixing in position Acoustical Panelling made from Fabric wrapped Compressed polyester fibre nonwoven 9 mm panels on, 50 x 50 mm sal-wood frame of 600 x 600 c to c having wooden supports from wall of required length, in front of 1000 gsm synthetic wool 50 mm thick with chicken mesh on wall side, including cost of required Cut-Outs, decorative mouldings / finishing-items / paint and Scaffolding, as per Architectural and Acoustical Design and Instructions and Complete in all aspects.including all materials labour,finishing etc complete | 82.5 | m2 |  | 0
10.14 | Providing and fixing in position Gypsum board false ceiling with 12.5 mm thick Gypsum boards, screwed/fixed to the under structure of suspended G.I. Grid constructed and suspended from the main ceiling consisting of ceiling sections of size 25 x 50 mm maximum center to center distance of 600 milimetre perimeter channel and intermediate channels at maximum center to center distance 1200 milimetre galvanized grid should be fixed to reinforced cement concrete slab. The gypsum board should be fixed to galvanized iron grid with necessary screws. The boards should be taped and filled from underside to give smooth, seamless ceiling. The rate should include necessary additional ceiling sections and intermediate channels. Additional intermediate channels should be fixed to strap hangers for additional support to prevent strapping at every 1200 milimetre item to be completed in all respect including necessary sleeves for ducts finishing of joints cut outs, painting including labour, material, lifts etc. all complete. Cost to include that for all drops, facias for cove lighting, cutouts for lights and AC's, etc. | 1030 | m2 |  | 0
10.15 | Providing and fixing in position Acoustical Doors along with 150 x 150 mm teak wood frame, doors made from 50mm Teak wood frame 600 x600 c to c filled with 1000 Gsm synthetic wool 50mm thick and 3mm Tecsound from both sides, 12mm waterproof ply and veneer from both sides , including 150mm heavy duty SS hinges (Geze / Dorma or eq.) 4 no each leaf, with Door-closer (Dorma / Geze or eq.) including cost of required Cut-Outs, decorative mouldings / finishing-items / melamine polish & Scaffolding as per Architectural and Acoustical Design and Instructions and Complete in all aspects .including all materials labour,finishing etc complete | 6.3 | m2 |  | 0
10.16 | Removing doors and windows with frames and stacking the materials as directed with all leads, lifts etc. complete. | 18 | each |  | 0
10.17 | Providing & fixing of Casement openable/ fixed window of approved make with DGU. The extruded aluminium sections of Alloy 6063 tolerances confirming to DIN standard from approved raw material V2 / V4 as directed by Engineer in charge. | 56 | m2 |  | 0
10.18 | Providing and fixing in position Phenol bonded Bamboo wood flooring with planks of sizes 14mm thick, 1800 mm length (minium) and 130 mm wide (minimum), in approved colour, texture and finish, having Performance Appraisal certified (PAC) issued by Building Materials & Technology Promotion Council (BMTPC). The flooring shall be fixed with tongue and groove interlocking system, with underlayment of 4mm thick expanded poly ethylene foam sheets having density 40kg/One One Cubic Metre, over prepared surface with necessary quarter round planks of size 1900mm x 18mm and door reducer of size 1900mm x 44mm, whereever required. The bamboo wood planks shall have minimum density of 1000 kg/One One Cubic Metre & minimum Hardness 1000kgf. with Eco friendly UV coating, all complete as per direction of Engineer in -charge. Ground floor | 162 | m2 |  | 0
10.19 | Providing and fixing in position Under Deck insulation for metal deck using 1000 Gsm synthetic wool with fixed to deck using adhesive and chicken mesh. | 115 | m2 |  | 0
10.2 | Providing and Fixing Rollar Blinds AMI Make or approved make and shade of 38mm round Aluminium channel with Blackout fabric and tilting with chain (Ball) system with all necessary fixtures and fitting etc. complete. (Sample to be final by Engineer In-charge prior execution of work) | 56 | m2 |  | 0
20 | Electrical work |  |  |  | 0
20.1 | SITC of Primary Electric Light SITC of Primary Electric Light Point including the cost of 2 x 1.5 Sqmm + 1x 1.0 Sqmm FRLS copper wire from the electrical light fitting to the switch board, pulled & laid in 20 mm dia PVC conduits (shared) & the cost of 6A modular switch with concealed box & cover plate (Shared) as per drawings & directions. Length of Primary point about 30 feet | 50 | each |  | 0
20.2 | Same as above but for Secondary Light Same as above but for Secondary Light point looped from the above mentiioned Primary point. Distance from primary to secondary point about 10 feet | 50 | each |  | 0
20.3 | SITC of Primary 5A Power Point SITC of Primary 5A Power Point including the cost of 2 x 2.5 Sqmm + 1x 1.5 Sqmm FRLS copper wire from the 5A Socket to the switch board, pulled & laid in 20 mm dia PVC conduits (Shared) laid under floor by cutting chases in the tiled floor & concealing the same with cement mortar 1:6 in proper line & level & the cost of 6A modular switch/ Socket outlet with concealed box & cover plate (Shared) as per drawings & directions | 24 | each |  | 0
20.4 | Same as above but for Secondary Same as above but for Secondary power point looped from the above mentiioned Primary point. | 24 | each |  | 0
20.5 | SITC of Primary 15A Power Point SITC of Primary 15A Power Point including the cost of 2 x 4 Sqmm + 1x 2.5 Sqmm FRLS copper wire from the 15A Socket to the switch board, pulled & laid in 20 mm dia PVC conduits (Shared) laid under floor by cutting chases in the tiled floor & concealing the same with cement mortar 1:6 in proper line & level & the cost of 16A modular switch/ Socket outlet with concealed box & cover plate (Shared) as per drawings & directions | 8 | each |  | 0
20.6 | Same as above but for Secondary Same as above but for Secondary power point looped from the above mentiioned Primary point. | 8 | each |  | 0
20.7 | Supplying and erecting underfloor Supplying and erecting underfloor junction box of size 300mm x300mm x55 mm. with flush finish powder coated appearance having knock outs for UPVC duct entry of size 60x25 mm and 95x35 mm ducts complete | 8 | each |  | 0
20.8 | Supplying & erecting mains/ Supplying & erecting mains/ Circuit wiring with 2x2.5 sq.mm.and earth wire 1.5 sq.mm FRLS PVC copper wire in rigid PVC conduit min.20mm dia. | 240 | m |  | 0
20.9 | Supplying & erecting mains/ Supplying & erecting mains/ circuit wiring with 2x4 sq.mm.and earth wire 2.5 sq.mm FRLS PVC copper wire in rigid PVC conduit min.20mm dia, | 120 | m |  | 0
20.1 | Supplying & erecting mains/ Supplying & erecting mains/ circuit wiring with 2x6 sq.mm.and earth wire 4 sq.mm FRLS PVC copper wire in rigid PVC conduit min.20mm dia, | 240 | m |  | 0
20.11 | Supplying and erecting modular Supplying and erecting modular type bell-push 6A / 10A ISI mark approved make duly erected on provided plate and box with wiring connections complete | 1 | each |  | 0
20.12 | Supplying and erecting Telephone Supplying and erecting Telephone point including modular type telephone socket one gang with safety shutter ISI mark approved make duly erected on provided plate and box with wiring connections complete with wiring in CAT 6 cable laid in 20 mm dia PVc conduits (Shared) from outlet to Krone box (Length about 25 feet) | 8 | each |  | 0
20.13 | Supplying and erecting modular Supplying and erecting modular type computer point with Jack RJ 45 with safety shutter ISI mark approved make duly erected on provided plate and box with wiring connections complete with wiring in CAT 6 cable laid in 20 mm dia PVC conduits (Shared) from out let to Switch/ Server & including patching the same at both ends & labelling. | 8 | each |  | 0
20.14 | Supplying and erecting modular Supplying and erecting modular type buzzer 230 / 250V ISI mark approved make duly erected on provided plate and box with wiring connections complete | 1 | each |  | 0
20.15 | Supplying, erecting & commissioning Supplying, erecting & commissioning Main Distribution Frame (MDF) Box 50x50 pairs as per specification No. WG-TW | 2 | each |  | 0
20.16 | Supplying, erecting & commissioning Supplying, erecting & commissioning Junction box suitable for 10 pairs as per specification No. WG- TW | 2 | each |  | 0
20.17 | Supplying and erecting FR grade, Supplying and erecting FR grade, PVC armoured multimode armoured multimode Optical Fibre Cable with 6 fibres, with core dia 50/125 μm (OM3) suitable for 1 GBps ethernet distance at 850 nm of wavelength, on wall/ceiling or laid in provided pipe/ trench as per specification No. WG-COC/OFC LSZH | 100 | m |  | 0
20.18 | Dismantling the existing light, Dismantling the existing light, fan, bell, clock, independent plug point, wiring including circuit mains of all types along with accessories etc.complete as per specification No: WG-DM/PW | 50 | each |  | 0
20.19 | Dismantling the existing Telephone Dismantling the existing Telephone / Lan / Wan / TV cables and wires of all sizes along with casing- capping / conduit complete as per specification No: WG-DM/PW | 20 | m |  | 0
20.2 | Dismantling the existing Aluminium Dismantling the existing Aluminium/copper mains,submains wiring upto 10 sq.mm. along with accessories etc.Complete as per specification No: WG-DM/PW | 50 | m |  | 0
20.21 | Supplying and erecting square Supplying and erecting square shaped CRCA / die- cast aluminium powder coated housing LED Panel light 600X600mm of PREMIUM RANGE suitable for upto 45 to 48 W with provision for plane front frame with translucent cover fixed to the housing complete | 10 | each |  | 0
20.22 | Supplying and erecting square Supplying and erecting square shaped CRCA / die- cast aluminium powder coated housing LED Panel light 250X250mm of PREMIUM RANGE suitable for upto 18 to 20 W with provision for plane front frame with translucent cover fixed to the housing complete | 48 | each |  | 0
20.23 | Supplying and erecting T8 Supplying and erecting T8 Fluroscent tube day light 1200mm 36 W | 4 | each |  | 0
20.24 | Supplying erecting testing Supplying erecting testing & commissioning of 20W LED wall mounted bracket/ picture light type fitting including all fittinngs & fixtures (Basic Price of Chandelier Rs 2,000/- per fitting) | 16 | each |  | 0
20.25 | Supplying erecting testing Supplying & erecting triple pole and neutral distribution board (TPNDB), 3 pole/ 4 pole MCCB as incomer & outgoing SP MCB (12 poles) or TP MCB of 4 ways (12 poles), with door, 1.2mm thickness, surface/flush mounted, on iron/GI frame (vertical busbar type) | 1 | each |  | 0
20.26 | Supplying & erecting triple pole Supplying & erecting triple pole and neutral distribution board (TPNDB), 3 pole/ 4 pole MCCB as incomer & outgoing SP MCB (12 poles) or TP MCB of 6 ways (18 poles), with door, 1.2mm thickness, surface/flush mounted, on iron/GI frame (vertical busbar type) | 1 | each |  | 0
20.27 | Supplying & erecting triple pole Supplying & erecting triple pole and neutral distribution board (TPNDB), 3 pole/4 pole MCCB as incomer & outgoing SP MCB (24 poles) or TP MCB of 8 ways (24 poles), with door, 1.2mm thickness, surface/flush mounted, on iron/GI frame (vertical busbar type) | 2 | each |  | 0
20.28 | Supplying & erecting triple pole Supplying & erecting triple pole and neutral distribution board (TPNDB), 3 pole/4 pole MCCB as incomer & outgoing SP MCB (36 poles) or TP MCB of 12 ways (36 poles), with door, 1.2mm thickness, surface/flush mounted, on iron/GI frame (vertical busbar type) | 1 | each |  | 0
20.29 | Supplying & erecting triple pole Supplying, erecting & marking SPN MCB 6Ato 32A, C- series (for motor/power/ Lighting) in provided distribution board | 48 | each |  | 0
20.3 | Supplying, erecting & marking Supplying, erecting & marking TPN MCB 16A, C- Series in provided distribution board | 1 | each |  | 0
20.31 | Supplying, erecting & marking Supplying, erecting & marking TPN MCB 40A to 63A, C- Series in provided distribution board | 2 | each |  | 0
20.32 | Providing & erecting 4 Pole MCCB Providing & erecting 4 Pole MCCB upto 200A, 415V capacity with S.C. rating 25 kA (Ics=100% of Icu), thermal setting with provided leads on iron frame/wooden board | 1 | each |  | 0
20.33 | Supplying, erecting & terminating Supplying, erecting & terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3½ core 25 sq. mm. copper conductor complete erected with glands & lugs, on wall/ trusses/ pole or laid in provided trench/ pipe | 50 | m |  | 0
20.34 | Supplying, erecting & terminating Supplying, erecting & terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3½ core 50 sq. mm. copper conductor complete erected with glands & lugs, on wall/ trusses/ pole or laid in provided trench/ pipe | 1 | each |  | 0
20.35 | Supplying, erecting & terminating Supplying, erecting & terminating FR XLPE insulated, galvanised steel formed wire armoured (strip) cable 1100 V, 3½ core 150 sq. mm. aluminium conductor complete erected with glands & lugs, on wall/ trusses/pole or laid in provided trench/ pipe | 1 | each |  | 0
20.36 | Providing earthing with Copper Providing earthing with Copper earth plate size 60 x 60 x 0.315 cm with funnel with a wire mesh for watering and brick masonry block C.l. cover with minimum 25 kg of maintenance free earth conductivity enhancing mineral earthing compound complete with all materials, testing & recording the results as per specification no ESE -LA | 4 | each |  | 0
20.37 | Supplying and erecting G.I. strip Supplying and erecting G.I. strip of required size used for earthing on wall and/or any other purpose with necessary GI clamps fixed on wall painted with bituminous paint in an approved manner with joint required. as per specification No (EA-EP). | 30 | kg |  | 0
20.38 | Supplying and erecting Annealed Supplying and erecting Annealed bare copper wire of high purity of different sizes used for earthing on wall with necessary copper clamps fixed on wall/ cable/conduit with screws in an approved manner. | 30 | kg |  | 0
20.39 | Providing, fixing, testing & Providing, fixing, testing & commissioning open LED lighting strip, 20 W/ Rm of approved type & make as per directions. | 80 | m |  | 0
20.4 | Providing, fixing, testing & Providing, fixing, testing & commissioning Neon Flex LED lighting strip, 20 W/ Rm of approved type & make as per directions. | 40 | m |  | 0
20.41 | Providing, Fixing, Testing Providing, Fixing, Testing & Commissioning HDMI cable including connectors at both ends | 40 | m |  | 0
20.42 | Providing, Fixing, Testing Providing, Fixing, Testing & Commissioning RG 6 cable including connectors at both ends | 40 | m |  | 0
20.43 | SITC 20 pair Jelly filled Armoured SITC 20 pair Jelly filled Armoured telephone cable | 30 | m |  | 0
20.44 | Supply & Laying 4+1 Wire for CCTV Supply & Laying 4+1 Wire for CCTV | 100 | m |  | 0
20.45 | Supply & Inst of 8 Module POPUP Box Supply & Inst of 8 Module POPUP Box | 1 | each |  | 0
20.46 | Supply & Laying of 1Rmt Patch Supply & Laying of 1Rmt Patch cord Wire for Data | 8 | each |  | 0
20.47 | Supplying and erecting fresh Supplying and erecting fresh air cum exhaust fan of light duty 250 V A.C. 50 cycles 300mm. 1400 RPM rust proof body & blades, wire mesh, duly erected<(>,<)> complete. | 1 | each |  | 0
20.48 | Supplying and erecting energy Supplying and erecting energy saving ceiling fan 230 V A.C. 50 cycles 1200 mm complete erected in position | 1 | each |  | 0
20.49 | SITC of External Light points SITC of External Light points including the cost of 3 core 1.5 Sqmm Armoured Cu cable for point wiring (approximate length per point 25 meters) including the cost of post top lantern with 36 W LED light bulb, mounted on a base of RCC pedestal, connected to 20A SPMCB in the External DB. | 8 | each |  | 0
20.5 | Same as above but for Secondary Same as above but for Secondary Light point (Approximate length of cable 6 meters) | 8 | each |  | 0
30 | PA, FIRE DETECTION & CCTV SYSTEM FOR DA |  |  |  | 0
30.1 | Supply, Installation, Testing & Commissioning of Addressable Intelligent multisensor detector with two inbuilt optical smoke sensors with backward & forward scattering light angles as well as additional heat detector sensor with decentralise intelligence, soft addressable and/ or hard addressable Photo thermal type with inbuilt fault isolator as per EN 54 / NFPA style 7 wiring complete with base as required . | 4 | each |  | 0
30.2 | Supply, Installation, Testing Commissioning of Addressable Intelligent Heat Detector with fixed & rate of rise temperature function with decentralise intelligence isolator as per EN 54 / NFPA style 7 wiring complete with base as required. | 2 | each |  | 0
30.3 | Supply, Installation, Testing & Commissioning of Addressable Intelligent optical detector with decentralise intelligence, automatic function self test, soft addressable and/or hard addressable Photo type with inbuilt fault isolator as per EN 54 / NFPA style 7 wiring complete with base as required | 1 | each |  | 0
30.4 | Supply, Installation, Testing & Commissioning of Addressable Manual Call Point soft addressable and/or hard B41 type with in built fault isolator as per NFPA style 7 wiring complete as required. B48 | 2 | each |  | 0
30.5 | Supply, Installation, Testing & Commissioning of Addressable transponder/ Monitor Modules for monitoring flow switches/Fire exit doors etc complete as required. | 2 | each |  | 0
30.6 | Supply, Installation, Testing & Commissioning of loop Powered Addressable Hooter (sound output of minimum 90 db )cum strobe strength of light 10 cd)complete as required. | 1 | each |  | 0
30.7 | Providing & Installing Response Indicato Providing & Installing Response Indicator | 1 | each |  | 0
30.8 | Supply and fixing of 2 Core Supply and fixing of 2 Core x 1.5 sq.mm. Copper conductor FR Cable (Orange) fixed on walls, witrh saddles and spacers all complete with hardwares. | 60 | m |  | 0
30.9 | Supply and fixing of 8 Core Supply and fixing of 8 Core x 1.5 sq.mm. Copper conductor FR Armoured Cable fixed on walls, witrh saddles and spacers all complete with hardwares. | 25 | m |  | 0
30.1 | Supply , installation , testing commssioning of 6W Ceiling Mount Speaker with backbox for mounting as per technical specifications. | 8 | each |  | 0
30.11 | Supply , installation , testing commssioning of 1000 W Power Amplifier complete as per technical specifications. | 2 | each |  | 0
30.12 | Supply , installation , testing commssioning of DVD/CD/MP3 with FM complete as per technical specifications. | 2 | each |  | 0
30.13 | Supply , installation , testing commssioning of 6W Volume Control Switch with ON OFF Control for Controlling the Speaker Volume at the User level. | 2 | each |  | 0
30.14 | Supply , installation , testing commssioning of the Rack of suitable design to house all the amplifiers accessories and ready for commissioning all complete floor mounting. | 2 | each |  | 0
30.15 | Supply , installation , testing commssioning of Console with facilitating annoucement of All Zone. | 2 | each |  | 0
30.16 | Supply , installation , testing commssioning of 40/36 wires in to be laid in GI , 14 G minimum 20 mm Conduit complete with all fixing accessories as per the specifications | 120 | m |  | 0
30.17 | Supply , installation , testing commssioning of the Music Fuse boxes complete with bottle tyupe fuses to control circuits at every floor level in GI enclosure all complete wall mounting. | 2 | each |  | 0
30.18 | Supply , installation , testing commssioning of the Main Music Fuse box at the Main console end to terminate floor circuit wires all complete with bottle tyupe fuses to control circuits at every floor level in GI enclosure all complete wall mounting. | 2 | each |  | 0
40 | HVAC lowside |  |  |  | 0
40.1 | Supplying, erecting, testing & commissioning fresh air intake system, ductable circular inline fresh air fan inlet unit having 1000 cfm capacity with maintaining the static pressure minimum 20mm suitable to operate on 1 phase, 230V, 50Hz, A.C. supply complete. | 2 | each |  | 0
40.2 | Supplying and erecting circular flexible/rigid PVC pipe duct of size 100mm dia, 4mm thickness with required couplers, reducers, T- joints, Y-joints elbows and necessary supports etc. with sealing with provided control/air flow regulating valves / dampers, filters at position complete. | 30 | m |  | 0
40.3 | Supplying and erecting an air flow regulating valves/dampers in provided flexible or rigid duct/pipe of 100 mm size with an alteration for existing flexible PVC pipe duct and necessary joints, sealing, couplings at position complete. | 2 | each |  | 0
40.4 | Carrying out core cutting of size 3" to 5" dia x 15" length in the C.C./rock/stone wall with the help of specialized core cutting machine in proper manner and finishing the site as original | 2 | each |  | 0
40.5 | supplying, laying/fixing, testing and commissioning of appropriate nominal refrigerant copper pipe of 15.9 mm dia (OD) for liquid line/suction line supply and return piping of suitable gauge (hard copper pipe for liquid main line and soft copper pipe for refrigerant) along with necessary supports, hangers, clamps, vibration isolators and fittings such as bends, tees, valves, gauges, strainers with insulation of 19mm thick elastomeric nitrile rubber along with application of multicoating of VRV/VRF piping for protection against mechanical damages, fungal growth, flame spread, water permeance and ultraviolet radiations with OEM standards of VRV/VRF air conditioning system complete. | 48 | m |  | 0
40.6 | Same as above but for 19.1 mm dia | 24 | m |  | 0
40.7 | Same as above but for 22.2 mm dia | 24 | m |  | 0
40.8 | Same as above but for 34.9 mm dia | 20 | m |  | 0
50 | HVAC Highside |  |  |  | 0
50.1 | Supplying, erecting, testing and commissioning of 6HP, VRF/VRV air conditioning system outdoor unit (ODU) complies type-IV OEM standards working on HFC refrigerant R410A or other required/suitable green equivalent refrigerant, for minimum cooling capacity as delivering 100% capacity at 47° C, non stop cooling even at 56° C and coefficient of performance (COP) 3.00 to 4.00, modular type vertical hot air discharge suitable for longer piping range upto 1000m operation in cooling mode with inverter/ digital VRF/VRV technology microprocessor based control compressor starter/control panel with scroll compressor, air cooled copper condenser coil of suitable shape for increasing maximum heat transfer area, rain protection cover, built in oil separator, accumulator and oil receiver, copper tube aluminium fin air cooled condenser, condenser fan with motor suitable for 415V±10%, 50 Hz, 3 phase power supply (all suitable for high ambient conditions), internal copper refrigerant piping, internal wiring and refrigerant, etc. all housed in powder coated weather proof cabinet complete | 2 | each |  | 0
50.2 | Supplying, erecting, testing and commissioning of VRF/VRV based ceiling suspended 4 Way cassette room/indoor unit (IDU- compact/standard size) of nominal cooling capacity 1.5TR (512 cfm) to 1.8TR (618 cfm) having EER as per BEE standards and specifications, suitable as per site requirement with swing louvers and adjustable blades from sides. IDU with drainage arrangements, fan, refrigerant liquid and refrigerant piping, cordless remotecontrol, and fresh air port etc. IDU shall have anti corrosive coating suitable for coastal area in all respects suitable to operate on 1-phase, 230V, 50Hz, AC supply complete. The unit consisting with any additional refrigerant and oil charge as per requirement during installation. | 8 | each | 0 | 0
| Total |  |  |  | 0
| GST 18 % |  |  |  | 0
| Total Including 18 % GST |  |  |  | 0